## Slide 1: Sprinkler Systems and Wood Trusses
Overview
Revised 3/23/2017

## Slide 2
SBCA has been the voice of the structural building components industry since 1983, providing educational programs and technical information, disseminating industry news, and facilitating networking opportunities for manufacturers of roof trusses, wall panels and floor trusses. SBCA endeavors to expand component manufacturers’ market share and enhance the professionalism of the component manufacturing industry.
Copyright © 2017 Structural Building Components Association.

## Slide 3: Introduction
The use of automatic Fire Sprinkler Systems in commercial, multifamily, and residential construction is intended to provide improved protection to a building and its contents from damage due to fire.
It is also intended to provide improved protection from injury to the building’s occupants.

## Slide 4: Introduction
Installed and functioning sprinkler systems can save lives and reduce property damage.
This is a win for everyone: the owner/occupant, firefighters, insurers, and the community in general.

## Slide 5: Introduction
SBCA supports universal building installation of sprinklers for all types of construction, provided they are cost effective and do not create a competitive advantage for one structural element over another.
A sprinkler system can even pay for itself through:
  Lower insurance costs
  Reduced corridor widths
  Less expensive wall and door assemblies
  Reduction or elimination of exit requirements
  Enhanced resale value

## Slide 6: Introduction
When Fire Sprinkler Systems are used with truss systems, it is essential to design the trusses to carry the additional dead load and required live loads imposed by the Fire Sprinkler System.
This presentation provides information to aid in the design of buildings with wood floor and/or roof trusses that are required to support Fire Sprinkler Systems.

## Slide 7: Key Definitions
NONCOMBUSTIBLE MATERIAL: A material that, in the form in which it is used and under the conditions anticipated, will not ignite, burn, support combustion, or release flammable vapors when subjected to fire or heat. Materials that are reported as passing ASTM E 136, Standard Test Method for Behavior of Materials in a Vertical Tube Furnace at 750°C, shall be considered noncombustible materials.
LIMITED-COMBUSTIBLE MATERIAL: Refers to a building construction material not complying with the definition of noncombustible material that, in the form in which it is used, has a potential heat value not exceeding 3500 Btu per lb. (8141 kJ/kg) (see NFPA 259), and includes either of the following: (1) materials having a structural base of noncombustible material, with a surfacing not exceeding a thickness of 1/8 in. (3.2 mm) that has a flame spread index not greater than 50; or (2) materials, in the form and thickness used having neither a flame spread index greater than 25 nor evidence of continued progressive combustion and of such composition that surfaces that would be exposed by cutting through the material on any plane would have neither a flame spread index greater than 25 nor evidence of continued progressive combustion when tested with ASTM E 84, Standard Test Method of Surface Burning Characteristic of Building Materials, or ANSI/UL 723, Standard Test Method of Surface Burning Characteristic of Building Materials.

## Slide 8: Background
The National Fire Protection Association (NFPA) is an international non-profit organization advocating fire prevention and safety.
The purpose of the NFPA sprinkler system standards is:
  To fairly evaluate construction practices and materials
  To define methods to best protect the occupants, the contents, and the structure in the event of fire

## Slide 9: Background
The NFPA publishes three sprinkler installation standards:
  NFPA 13 – The over-arching standard for sprinkler system protection
  NFPA 13D – One- and Two-family dwellings and manufactured homes
  NFPA 13R – Up to four-story multi-family residential buildings
Because the implementation of NFPA 13 was deemed cost-prohibitive in residential construction, two residentially oriented standards were created.

## Slide 10: Background
The NFPA standards are designed with two considerations:
  Life protection (The primary consideration in residential sprinkler system design)
  Property protection (Contents and/or structure - generally dominant in non-residential design)

## Slide 11: Background
The information in this presentation is applicable to the 2010 or 2013 editions of the NFPA standards, as referenced by the 2012 and 2015 versions of the model codes respectively.
It is intended to provide general guidance and does not represent the full complexity of the NFPA standards.
NFPA 13- Standards Referenced in the Model Codes |  |  |  | 
 | 13 | 13D | 13R | NFPA editions referenced
IBC 2006 | x | x | x | 2002
IRC 2006 | x |  |  | 2002
IBC 2009 | x | x | x | 2007
IRC 2009 | x | x |  | 2007
IBC 2012 | x | x | X | 2010
IRC 2012 | x | x |  | 2010
IBC 2015 | x | x | x | 2013
IRC 2015 | x | x |  | 2013

## Slide 12: Background
As metal plate connected wood truss usage has become more prevalent in all construction types, it is essential for the Building Designer to consider the loads imposed on the truss system and provide the Truss Designer with this information.
This allows the Truss Designer to make provisions in the truss design for the structural effects of the Fire Sprinkler System.

## Slide 13: Background
The open webbing of truss construction makes it highly compatible with other building trades.
Water lines for sprinkler systems can be run through the open webbing making maximum use of the available space without the loss of headroom and eliminating costs associated with drilling.

## Slide 14: Background
Occasionally, a building’s use or its contents demand a Fire Sprinkler System with special layout requirements and heavy main waterlines that cannot be compromised.
Truss construction can easily be manipulated with adjustments to panel lengths and web configurations to accommodate most special requirements.

## Slide 15: Application – NFPA 13D
Sprinklers shall be installed in all locations per the 13D requirements except the following:
  Bathrooms 55 ft2 and less.
  Closets 24 ft2 and less.
  Garages, open attached porches, carports and similar structures.
  Attics, floor/ceiling spaces, crawl spaces, and other concealed spaces that are not used or intended for living purposes and do not contained fuel-fired appliances.
  Covered unheated projections at entrances that are not the only means of egress.
  Ceiling pockets where the following conditions are met:
    Total volume of all unprotected ceiling pockets in a compartment does not exceed 100 ft2.
    The entire floor under the unprotected pocket is protected by the sprinklers at the lower ceiling level.
    The interior finish of the unprotected pocket is noncombustible or limited-combustible material.
    Skylights not exceeding 32 ft2 shall be permitted to have a plastic cover.
  Closets in garages and exterior closets where there is no unprotected penetration into the dwelling unit.

## Slide 16: Application – NFPA 13D
NOTE: Although basements are not excluded, a basement may be sprinklered as if the ceiling were finished.
Sprinkler Hanger Requirements:
  NFPA 13D has its own specific sprinkler hanger requirements.
  Since most residential sprinkler systems use the domestic water system, little or no extra design loading is required for roof or floor systems.

## Slide 17: Application – NFPA 13R
NFPA 13R - Multi-Family 4 stories or Less (2013 adds not exceeding 60 ft above grade plane)
  This category includes:
    Apartment buildings and condominiums.
    Lodging and rooming houses.
    Board and care facilities (slow evacuation type with 16 or fewer occupants and prompt evacuation type).
    Hotels, motels, and dormitories.

## Slide 18: Application – NFPA 13R
NOTE: some building code editions allow a 2 hour separation wall to divide larger multi-family buildings into one- and two-family dwellings allowing them then to be sprinklered per NFPA 13D requirements.

## Slide 19: Application – NFPA 13R
All areas are to be sprinklered except the following :
  Bathrooms 55 ft2 and less.
  Closets or pantries within dwelling unit 24 ft2 and less, least dimension does not exceed 3 ft, walls & ceiling covered with noncombustible or limited-combustible materials.
    Except for closets within dwelling unit used for heating and air-conditioning equipment (2013 adds washers, dryers or water heaters).
  Porches, balconies, corridors, and stairs that are open and attached (2013 adds porte cocheres).
    2013 adds: sprinklers are required for roofed exterior balconies or decks and ground floor patios in buildings of Type V Construction.
    2013 adds: requirements for sidewall sprinkler installation
  Attics, penthouse equipment rooms, elevator machine rooms, concealed spaces containing only dwelling unit ventilation equipment, crawl spaces, floor/ceiling spaces, noncombustible elevator shafts, and other concealed spaces that are not intended for living purposes or storage and do not contain fuel-fired equipment.
    If fuel-fired equipment is present, at least one quick-response intermediate temperature sprinkler is required.
  Closets on exterior balconies and exterior breezeways/corridors as long as there are no penetrations into dwelling unit.
    2013 adds: requirements for interior stairwells and spaces below them.

## Slide 20: Application – NFPA 13R
Sprinkler Hanger Requirements:
  Sprinkler hangers follow NFPA 13 standard requirements.
  Roof and floor design loads must be adjusted for sprinkler system weights
NOTE: where good design allows, there can be an economic advantage to designing a building to fit within the requirements of NFPA 13R rather than NFPA 13.
  However, some code jurisdictions require NFPA 13 protection for buildings in this category.

## Slide 21: Application – NFPA 13
Everything not covered by NFPA 13D or 13R follows the NFPA 13 standard.
A Roof/Ceiling or Floor/Ceiling construction can be constructed either in an open space environment or be constructed with ceilings that enclose the structural members and create concealed spaces within the floor or roof assemblies.

## Slide 22: Application – NFPA 13
There are two categories of construction type defined to determine the spacing and positioning rules for sprinklers:
  OBSTRUCTED CONSTRUCTION is construction where beams, trusses, or other members impede heat flow or water distribution in a manner that materially affects the ability of sprinklers to control or suppress a fire.
  UNOBSTRUCTED CONSTRUCTION: Construction where beams, trusses, or other members do NOT impede heat flow or water distribution in a manner that materially affects the ability of sprinklers to control or suppress a fire.
    Unobstructed construction has horizontal structural members that are not solid, where the openings are at least 70% of the cross-section area and the depth of the member does not exceed the least dimension of the openings,
    Or all construction types where the spacing of structural members exceeds 7-1/2 ft o.c.

## Slide 23: Application
Examples of OBSTRUCTED CONSTRUCTION include:
  Beam and Girder – spaced 3' to 7.5' on center and 4" or greater in depth.
  Composite Wood Joists (I-Joist) requiring fire-stopping so channels do not exceed 300 ft2
  Panel where spacing of structural members creates panels of less than 300 ft2.
  Semi-Mill (modified heavy timber) with greater column spacing and beams resting on girders.
  Wood Joists (2x or 4x wide max and 14" deep max) regardless of spacing. 2013 adds: wood joists may exceed 14” depth.

## Slide 24: Application
More examples of OBSTRUCTED CONSTRUCTION:
  Bar joists that are 30% obstructed
  Steel Purlin construction
  2013 adds: Truss Construction (wood or steel) parallel or pitched chord members constructed by open web members with top and bottom members greater than 4” in depth
  2013 adds: Bar Joist Construction (wood or steel) with top and bottom chords greater than 4” in depth

## Slide 25: Application
Examples of UNOBSTRUCTED CONSTRUCTION include:
  Any construction where supporting members are spaced 7.5' or more on center.
  Where spacing is less than 7.5' on center, any structural member that is not solid and where openings are at least 70% of cross section and the depth does not exceed the least dimension of the openings.

## Slide 26: Application
More examples of UNOBSTRUCTED CONSTRUCTION:
  Bar Joists (steel or wood) with top and bottom chords not exceeding 4” in depth
  Open Grid Ceilings
  Smooth Ceilings (as detailed)
  Standard Mill – heavy timber construction
  Truss Construction (wood or steel) parallel or pitched chord with bottom chords not exceeding 4” in depth

## Slide 27: Application
70% RULE
  Where spacing is less than 7.5' on center, any structural member that is not solid and where openings are at least 70% of cross section and the depth does not exceed the least dimension of the openings is considered unobstructed construction.
If the assembly is constructed as a floor/ceiling or roof/ceiling arrangement and is partially or wholly enclosed by combustible construction, the concealed space may be required to be protected by sprinklers.

## Slide 28: Application
CONCEALED COMBUSTIBLE SPACES, exceptions to the requirement for sprinklers in combustible floor/ceiling or roof/ceiling concealed spaces are allowed where the space is:
  Formed by studs or joists with less than 6" between edges.
  Formed by bar joists with less than 6" between roof/floor and ceiling.
  Formed by ceilings attached to or within 6" of wood joists.
  Formed by ceilings directly attached to composite wood joists provided joist channel is fire-stopped into volumes not exceeding 160 ft3 with material equal to that of the webs.
  Entirely filled with non-combustible insulation*. 2013 adds: a maximum 2” air gap at top of space is permitted.
  Within wood or composite joist construction with insulation filling space from ceiling to bottom of joist and in composite wood construction fire stopped into volumes not exceeding 160 ft3 with material equal to that of the webs.
  Over isolated small rooms not exceeding 55 ft2 in area
  Created with rigid materials with any exposed surface having a flame spread rating of 25 or less.*
  Constructed entirely of fire-retardant treated wood as defined by NFPA 703.*
  Noncombustible construction having exposed combustible insulation where the heat content of the facing and substrate does not exceed 1000 BTU/ft2.
NOTE - * applies to truss systems

## Slide 29: Application
More examples of CONCEALED COMBUSTIBLE SPACES:
  Created by insulation laid directly on top of or within the ceiling joists in an otherwise sprinklered attic.
  A pipe chase under 12 ft2 formed by studs or wood joists, provided they are fire stopped at each floor and contain no sources of ignition.
  Exterior columns under 10 ft2 in area formed by studs or wood joist, supporting exterior canopies that are fully protected with a sprinkler system.
  Noncombustible or limited-combustible suspended ceilings suspended from wood joists or composite wood joists, wood bar joists or wood trusses having insulation, where the heat content of the facing and substrate does not exceed 1000 BTU/ft2, filling the gap between the structural members and which have sprinklers above the insulation*.
  Noncombustible or limited-combustible suspended ceilings suspended from wood joists or composite wood joists where the space between the members is filled with noncombustible batt insulation with a maximum 2” air space between the insulation and the roof decking.
  Soffits, eaves, overhangs & decorative frame elements made of combustible material not exceeding 4 ft in width or volume not exceeding 160 ft3 and which are separated from the interior of the building by noncombustible or limited-combustible material and which contain no unprotected penetrations to the interior of the building.
NOTE - * applies to truss systems

## Slide 30: Example – Unobstructed Construction – 70% Rule
The truss members in Figure 1 are 2x4’s oriented horizontally (4x2):
  Area of the panel = 24" x 30" = 720 in2
  Chords = 2 x (30" x 1.5") = 90 in2
  Webs = 2 x (25.81" x 1.5") = 77 in2
  Total area = 90 + 77 = 167 in2
  Area of panel divided by obstructed area = 167/720 = 0.233 or 23%
The panel is 77% open, therefore this configuration would be considered 'Unobstructed Construction.'

## Slide 31: Example – Obstructed Construction
The truss members in the Figure 2 are 2x4’s oriented vertically (2x4):
  Area of the panel = 24" x 30" = 720 in2
  Chords = 2 x (30" x 3.5") = 210 in2
  Webs = 2 x (25.81" x 3.5") = 181 in2
  Total area = 210 + 181 = 391 in2
  Area of panel divided by obstructed area = 391/720 = 0.543 or 54%
The panel is 46% open, therefore this configuration would be considered 'Obstructed Construction.'

## Slide 32: Application – Design Load Considerations
The Building Designer must provide adequate dead load information, including the weight of the water filled pipe (generally in psf) and attachment locations.
Installation live loads must also be taken into account.
See SRR 1504-02 for more information

## Slide 33: Application – Design Load Considerations
It is generally best to support the sprinkler system from the top chord of the truss.
When bottom chord attachment is required, the Truss Manufacturer must make special provisions.
Trusses can support significantly higher loads at panel points than in the spaces between panel points.

## Slide 34: Application – Design Load Considerations
The location of the pipe support relative to the panel points of the truss is critical for the design.
Once the support connection types and points have been determined, it is critical that they are followed during the installation process.

## Slide 35: Application
Smaller point loads are generally designed to be carried by each truss.
However, the larger point loads created by large diameter sprinkler lines, significant risers and lines running parallel to trusses may require very specific attachment points or additional members.
Refer to NFPA 13, Chapter 9 and the Metal Plate Connected Wood Truss Handbook for further support information.

## Slide 36: Conditions of Use
Because of the variation in the adoption of the NFPA standards into national, regional, state, and local building codes, the design professional is responsible for understanding and designing to the governing local code.
Regardless of whether a sprinkler system is installed or not, smoke detectors, draft and firestop construction, and rated assemblies must be included as required by the governing building code.

## Slide 37: Conditions of Use
Exceptions to sprinklering certain areas may be allowed, but the level of safety is not equivalent when compared with a fully sprinklered building.
  However, the building is still considered sprinklered throughout as required by the model codes.

## Slide 38: Conditions of Use
Special sprinklers have been developed for specific applications in concealed roof/ceiling or floor/ceiling cases where trusses are used.
They address protection for flat concealed spaces as well as pitched roof attic spaces, including hipped roofs.

## Slide 39: References
ANSI/AWC National Design Specification® (NDS®) for Wood Construction, 2012, by the American Wood Council
ANSI/TPI 1 National Design Standard for Metal Plate Connected Wood Truss Construction, 2007, by Truss Plate Institute
ASCE/SEI 7, Minimum Design Loads for Buildings and Other Structures, 2010, by the American Society of Civil Engineers and the Structural Engineering Institute
International Building Code, 2012 & 2015, by the International Code Council
International Residential Code, 2012 & 2015, by the International Code Council

## Slide 40: References
NFPA 13, Standard for the Installation of Sprinkler Systems, 2010 and 2013, by the National Fire Protection Association
NFPA 13R, Standard for the Installation of Sprinkler Systems in Residential Occupancies Up to and Including Four Stories in Height, 2010 and 2013, by the National Fire Protection Association
NFPA 13D, Standard for the Installation of Sprinkler Systems in One- and Two-Family Dwellings and Manufactured Homes, 2010 and 2013, by the National Fire Protection Association
  NOTE: NFPA Standards may be viewed for free at the NFPA Free Access site by signing in.
Metal Plate Connected Wood Truss Handbook, Third Edition, 2002, Chapter 17 Part 1 & Part 2, by the Structural Building Component Association, 6300 Enterprise Lane, Madison, WI 53719.